## FIGURE 2
686.7121 | LIGHTING | 1.808%
25514.0952 | MOTORS | 67.17%
9004.5 | AIR-CONDITIONING | 23.71%
2777.4307 | AIR COMPRESSORS | 7.312%
37982.7381

## FIGURE 1
EQUIPMENT LIST AND ENERGY BALANCE
Electric
LIGHTING
Location and Equipment name | W | Fixtures | Lamps per Fixture | Est. hours per year lights used | Est. hours per year area used | A/C (Y/N) | Estimated ballast factor |  | kW | kWh | Estimated Annual Cost ($/yr)
Lighting | [8 empty] | =kW/lamp x Number of Fixtures x Number of Lamps per fixture x (Ballast factor + 1) | =total kW x Estimated hours per year | = kW x $/kW/month x 12 months/yr + kWh x $/kWh
Office
Lighting line item
Conference room, 8' fluorescent | 60 | 2 | 2 | 2025 | 500 | Y | 1.15 |  | 0.276 | 558.9 | 54.0846
Lobby and hallway, 8' fluorescent | 60 | 4 | 2 | 2025 | 2025 | Y | 1.15 |  | 0.552 | 1117.8 | 108.1692
Office lighting sub-total: | [8 empty] | 0.828 | 1676.7 | 162.2539
Saw Mill
Saw mill, 8' fluorescent | 95 | 7 | 2 | 2025 | 2025 | N | 1.15 |  | 1.5295 | 3097.2375 | 250.7138
Saw shack, incandescent | 100 | 1 | 1 | 2025 | 2025 | Y | 1 |  | 0.1 | 202.5 | 16.3919
Head saw, halogen spotlight | 95 | 1 | 2 | 2025 | 2025 | N | 1 |  | 0.19 | 384.75 | 31.1446
Saw mill, HPS | 150 | 8 | 1 | 2025 | 2025 | N | 1.15 |  | 1.38 | 2794.5 | 226.208
Saw mill lighting sub-total: | [8 empty] | 3.1995 | 6478.9875 | 524.4583
LIGHTING TOTALS: | [8 empty] | 4.0275 | 8155.6875 | 686.7121
MOTORS
Location and Equipment Name | HP (rated) | units | hours per year | lf | uf | df | Est. Efficiency | Number of Belts | kW | kWh | Estimated Annual Cost ($/yr)
Saw Mill | [8 empty] | = (Hp/unit x number of units x lf x 0.746 x df)/ Efficiency | = kW x hours per year x uf / df | = kW x $/kW/month x 12 months/yr + kWh x $/kWh
Motor line item
Chipping edger | 75 | 2 | 2025 | 0.4 | 0.6 | 0.9 | 0.941 | 8 | 42.8098 | 57793.1987 | 5700.9163
Head saw | 100 | 1 | 2025 | 0.4 | 0.6 | 0.9 | 0.945 | 4 | 28.419 | 38365.7143 | 3784.5236
Log trimmer | 15 | 1 | 2025 | 0.4 | 0.6 | 0.9 | 0.91 | 0 | 4.4268 | 5976.1978 | 589.5123
Conveyor | 5 | 2 | 2025 | 0.4 | 0.8 | 1 | 0.875 | 0 | 3.4103 | 5524.6629 | 496.0897
Saw mill motors sub-total: | [8 empty] | 79.0659 | 107659.7737 | 10571.0419
FIGURE 1 - ENERGY BALANCE -- ELECTRICAL EQUIPMENT
Miscellaneous
Drying room fans | 2 | 8 | 8760 | 0.9 | 0.6 | 1 | 0.84 | 1 | 12.7886 | 67216.7314 | 4465.4533
Drying room fans | 7.5 | 6 | 8760 | 0.8 | 0.6 | 1 | 0.895 | 1 | 30.0067 | 157715.2358 | 10477.6
Miscellaneous motors sub-total: | [8 empty] | 42.7953 | 224931.9672 | 14943.0533
MOTORS TOTALS: | [8 empty] | 121.8612 | 332591.7409 | 25514.0952
AIR-CONDITIONING
Location and Equipment name | Tons | units | SEER | df | hours per year |  |  |  | kW | kWh | Estimated Annual Cost ($/yr)
A/C line item | [8 empty] | = tons/unit x number of units x 12 x df / SEER | = kW x CDD / df | = kW x $/kW/month x 12 months/yr + kWh x $/kWh
Scragger booth, window unit | 1 | 3 | 8 | 1 | 2000 |  |  |  | 4.5 | 9000 | 732.5097
A/C sub-total: | 3 |  | 8
Average COP: |  |  | 2.3447
A/C TOTALS: | [8 empty] | 4.5 | 9000 | 9004.5
AIR COMPRESSORS
Location and Equipment Name | HP (rated) | units | hours per year | lf | uf | df | Estimated Efficiency | Number of Belts | kW | kWh | Estimated Annual Cost ($/yr)
Air Compressors line item | [8 empty] | = (Hp x number of units x lf x 0.746 x df)/ Efficiency | = kW x hours per year x uf / df | = kW x $/kW/month x 12 months/yr + kWh x $/kWh
Maintenance shop | 15 | 1 | 2025 | 0.4 | 0.8 | 1 | 0.91 | 0 | 4.9187 | 7968.2637 | 869.3934
Saw mill | 20 | 2 | 2025 | 0.4 | 0.8 | 1 | 0.91 | 3 | 13.1165 | 21248.7033 | 1908.0374
AIR COMPRESSOR TOTALS | [8 empty] | 18.0352 | 29216.967 | 2777.4307
CALCULATED FIGURES | [8 empty] | 148.4239 | 378964.3954 | 37982.7381
ESTIMATED MISCELLANEOUS | [5 empty] | 0.1 |  |  | 14.8424 | 37896.4395 | 3798.2738
TOTALS | [8 empty] | 163.2662 | 416860.8349 | 41781.0119
MIN ACTUAL kW | [8 empty] | 145
MAX ACTUAL kW | [8 empty] | 165
ACTUAL kWh ¦ Cost | [9 empty] | 416900 | 41700
ERROR IN kWh ¦ Cost | [8 empty] | -1.051% | -0.009394% | 0.1943%
FIGURE 1 - ENERGY BALANCE -- ELECTRICAL EQUIPMENT